# Quick-Wall Flood Panels (WK Model# FB-QW) Specifications

## Part 1 – General

  - Description: Provide flood barrier(s) with side frames and all operating components in accordance with contract specifications and approved drawings.

  - Acceptable Manufacturers: Flood barrier shall be as manufactured by Walz & Krenzer, Inc (203-267-5712; sales@wkdoors.com).

  - Standards: Comply with the provisions of the following (as applicable):

- AISC “Specifications for Design, Fabrication, and Erection of Structural Steel for Buildings”.

- The Aluminum Assoc. “Aluminum Design Manual”.

- AWS Structural Welding Code D1.1, D1.2, D1.3, D1.6.

- ASME Structural Welding Code Section IX.

- FEMA Bulletin 3-93, #102 & #114.

  - Submittals:

- Manufacturers Data: Submit installation and maintenance manuals for flood barrier.

- Shop Drawings: Submit shop drawings approved by licensed Professional Engineer for flood barriers including dimensional plans, elevations, sections, details for all mountings/connections, and parts list.

- Calculations (optional for critical applications): Submit calculations approved by licensed Professional Engineer verifying the flood barrier’s ability to withstand the design pressure loading.

- QA Submittals: Submit test reports showing compliance with specified performance characteristics.

  - Qualifications: Manufacturer shall present evidence attesting to at least five years successful experience in the design and manufacture of similar closures.

## Part 2 – Products

- Product Description: Flood barrier shall be Model FB-QW as manufactured by Walz & Krenzer, Inc.

- Materials:

- Panel: custom extruded 6061-T6 aluminum shape.

- Frame: ASTM A-36 steel (options include aluminum and 304 or 316 stainless steel).

- Posts: custom extruded 6061-T6 aluminum shape.

- Latches: stainless steel sliding latch bolts.

- Gasket: Walz & Krenzer EPDM gaskets. Custom shapes for posts, logs and frames.

- Finish: extruded aluminum mill finish.

- Storage rack: aluminum or mild steel pallet.

- Design:

- Design Pressure: # (in feet of water). Specify seating (pushing gate closed) or unseating direction (pushing gate open).

- Side frames are custom fabricated to attach to existing wall geometry.

- Depending on floor surface, a bottom frame may not be required. Bottom gasket designed to seal against floor surface.

- Floor is to be flat within 1/16” between the posts with a typical spacing of 10 feet between posts.

- Bottom post frame is to be recessed into floor surface to achieve a flush sill. Depth of frame depends on the flood elevation.

- Slight leakage may occur in quick-wall design. Leakage rate is low and is comparable with other stop log type designs.

- Frames shall have mounting holes for expansion anchors (options include masonry subframe with welded anchors for embedment in concrete).

- Additional requirements such as hydrodynamic loads, impact loads and breaking wave loads shall be added as required by the specific application.

- Quality Assurance:

- Perform shop dimensional test and compare with drawings.

# Part 3 – Execution

- Fabrication:

- The finished product shall be rigid, neat in appearance, and free from all defects, warps, and buckles.  All exposed joints and corners shall be well rounded.

- The panel and frame shall be flat within 1/8” in any 6’ length.

- All butt welds in frame to be full penetration welds.

- Installation:

- Install flood barrier in accordance with manufacturer’s instructions and approved shop drawings.

- After installation, perform field operational test per manufacturer’s instructions to verify seal.

- Finish paint (if applicable) after installation.

- Warranty: Flood barrier shall operate satisfactorily and be free of defects in material and workmanship for a period of not less than one year from the date of delivery.